## Cables
ID	Designation	R20	X1	R0	X0	C1	I_adm	I_sc_1s	cond_material	insul_material	Diameter
Унікальна назва	Позначення	R1 (Ом/км) при 20°C	X1 (Ом/км)	R0 (Ом/км)	X0 (Ом/км)	C1 (нФ/км)	Допустимий тривалий струм (А)	Допустимий струм КЗ за 1 сек (кА)	Матеріал жили Cu/Al	Матеріал ізоляції PVC/XLPE/PI	Зовнішній діаметр (мм)
VVGng_2х1.5	ВВГнг 2х1.5	12,1	0,103	48,4	0,412		21	0,17	Cu	PVC	9,2	ВВГнг	1 кВ
VVGng_2х2.5	ВВГнг 2х2.5	7,41	0,098	29,6	0,392		27	0,28	Cu	PVC	10,2
VVGng_2х4	ВВГнг 2х4	4,61	0,091	18,4	0,364		36	0,45	Cu	PVC	11,3
VVGng_2x6	ВВГнг 2х6	3,08	0,088	12,3	0,352		46	0,68	Cu	PVC	12,5
VVGng_2x10	ВВГнг 2х10	1,83	0,084	7,32	0,336		63	1,13	Cu	PVC	14,5
VVGng_2x16	ВВГнг 2х16	1,15	0,081	4,6	0,324		84	1,81	Cu	PVC	16,8
VVGng_2x25	ВВГнг 2х25	0,727	0,079	2,91	0,316		112	2,83	Cu	PVC	20,2
VVGng_2x35	ВВГнг 2х35	0,524	0,077	2,1	0,308		137	3,96	Cu	PVC	22,4
VVGng_2x50	ВВГнг 2х50	0,387	0,076	1,55	0,304		167	5,65	Cu	PVC	25,6
VVGng_2x70	ВВГнг 2х70	0,268	0,074	1,07	0,296		211	7,91	Cu	PVC	28,8
VVGng_2x95	ВВГнг 2х95	0,193	0,073	0,77	0,292		261	10,7	Cu	PVC	32,4
VVGng_2x120	ВВГнг 2х120	0,153	0,072	0,61	0,288		302	13,6	Cu	PVC	36,5
VVGng_2x150	ВВГнг 2х150	0,124	0,072	0,5	0,288		346	17	Cu	PVC	40,2
VVGng_2x185	ВВГнг 2х185	0,099	0,071	0,4	0,284		397	20,9	Cu	PVC	44,8
VVGng_2x240	ВВГнг 2х240	0,075	0,071	0,3	0,284		472	27,1	Cu	PVC	51,2
AVVGng_2x2.5	АВВГнг 2х2.5	12,1	0,098	48,4	0,392		21	0,18	Al	PVC	10,2	АВВГнг
AVVGng_2x4	АВВГнг 2х4	7,41	0,091	29,6	0,364		29	0,29	Al	PVC	11,3
AVVGng_2x6	АВВГнг 2х6	4,91	0,088	19,6	0,352		37	0,44	Al	PVC	12,5
AVVGng_2x10	АВВГнг 2х10	3,08	0,084	12,3	0,336		50	0,73	Al	PVC	14,5
AVVGng_2x16	АВВГнг 2х16	1,91	0,081	7,64	0,324		67	1,17	Al	PVC	16,8
AVVGng_2x25	АВВГнг 2х25	1,2	0,079	4,8	0,316		87	1,83	Al	PVC	20,2
AVVGng_2x35	АВВГнг 2х35	0,868	0,077	3,47	0,308		106	2,56	Al	PVC	22,4
AVVGng_2x50	АВВГнг 2х50	0,641	0,076	2,56	0,304		126	3,65	Al	PVC	25,6
AVVGng_2x70	АВВГнг 2х70	0,443	0,074	1,77	0,296		161	5,11	Al	PVC	28,8
AVVGng_2x95	АВВГнг 2х95	0,32	0,073	1,28	0,292		197	6,94	Al	PVC	32,4
AVVGng_2x120	АВВГнг 2х120	0,253	0,072	1,01	0,288		229	8,76	Al	PVC	36,5
AVVGng_2x150	АВВГнг 2х150	0,206	0,072	0,82	0,288		261	11	Al	PVC	40,2
AVVGng_2x185	АВВГнг 2х185	0,164	0,071	0,66	0,284		302	13,5	Al	PVC	44,8
AVVGng_2x240	АВВГнг 2х240	0,125	0,071	0,5	0,284		359	17,5	Al	PVC	51,2
AABL_3х35_6	ААБл 3x35-6	0,89	0,087			310	115	2,41	Al	PI		ААБл	6 кВ
AABL_3х50_6	ААБл 3x50-6	0,62	0,083			350	140	3,45	Al	PI
AABL_3х70_6	ААБл 3x70-6	0,443	0,08			410	175	4,83	Al	PI
AABL_3х95_6	ААБл 3x95-6	0,326	0,078			460	215	6,55	Al	PI
AABL_3х120_6	ААБл 3x120-6	0,258	0,076			520	250	8,28	Al	PI
AABL_3х150_6	ААБл 3x150-6	0,206	0,074			570	285	10,35	Al	PI
AABL_3х185_6	ААБл 3x185-6	0,167	0,073			640	330	12,76	Al	PI
AABL_3х240_6	ААБл 3x240-6	0,129	0,071			730	395	16,56	Al	PI

## Batteries
ID	Designation	Capacity	U_nom	Ri_cell	I_sc_cell
Унікальна назва	Позначення	Емкость А*ч	Номинальное напряжение В	mOhm	Ток КЗ, А
BAE_8_OGi_200	BAE 8 OGi 200	234,00	1,95	0,49	4240,00
BAE_10_OGi_250	BAE 10 OGi 250	290,00	2,07	0,39	5310,00
BAE_12_OGi_300	BAE 12 OGi 300	345,00	2,01	0,33	6360,00
BAE_14_OGi_350	BAE 14 OGi 350	398,00	2,08	0,28	7430,00
BAE_5_OGi_400	BAE 5 OGi 400	422,00	2,13	0,23	9250,00

## CircuitBreakersCatalog
ID	Designation	Manufacturer	Series	Trip_unit_ID	In	Poles	P_loss_W	Icu
Унікальна назва	Позначення	Виробник	Серія	Крива	Номинальный ток А	Количество полюсов	Мощность рассеяния, Вт	Відключаюча здатність кА
C60H-DC_1A_2P_C	C60H-DC =500V 1А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	1	2	2,3	20
C60H-DC_2A_2P_C	C60H-DC =500V 2А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	2	2	2,6	20
C60H-DC_3A_2P_C	C60H-DC =500V 3А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	3	2	2,2	20
C60H-DC_4A_2P_C	C60H-DC =500V 4А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	4	2	2,4	20
C60H-DC_6A_2P_C	C60H-DC =500V 6А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	6	2	2,7	20
C60H-DC_10A_2P_C	C60H-DC =500V 10А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	10	2	1,8	20
C60H-DC_13A_2P_C	C60H-DC =500V 13А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	13	2	2,5	20
C60H-DC_16A_2P_C	C60H-DC =500V 16А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	16	2	2,5	20
C60H-DC_20A_2P_C	C60H-DC =500V 20А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	20	2	3	20
C60H-DC_25A_2P_C	C60H-DC =500V 25А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	25	2	3,1	20
C60H-DC_32A_2P_C	C60H-DC =500V 32А 2Р С	Schneider Electric	Acti9 C60H-DC	Curve_C_(DC)	32	2	3,5	20
iC60N_6A_1P_B	iC60N 1P 6A B	Schneider Electric	Acti9 iC60	Curve_B	6	1	2,7	10
iC60N_6A_2P_B	iC60N 2P 6A B	Schneider Electric	Acti9 iC60	Curve_B	6	2	2,7	10
iC60N_6A_3P_B	iC60N 3P 6A B	Schneider Electric	Acti9 iC60	Curve_B	6	3	2,7	10
iC60N_6A_3P_C	iC60N 3P 6A C	Schneider Electric	Acti9 iC60	Curve_C	6	3	2,7	15
iC60N_6A_3P_D	iC60N 3P 6A D	Schneider Electric	Acti9 iC60	Curve_D	6	3	2,7	20
NSX100B_3P_TM16D	NSX100B TM16D	Schneider Electric	COMPACT NSX	Curve_TM16D_AC	16	3	2,92	25
NSX100B_3P_TM63D	NSX100B TM63D	Schneider Electric	COMPACT NSX	Curve_TM63D_AC	63	3	8,61	25
NSX100B_3P_MA25	NSX100B MA25	Schneider Electric	COMPACT NSX	Curve_MA_AC	25	3	1,04	25
NSX100B_3P_ML_2.2_40A	NSX100B Micrologic 2.2 40A	Schneider Electric	COMPACT NSX	Curve_Micrologic_2.2	40	3	1,3	25
NSX630N_3P_ML_5.3_630A	NSX630N Micrologic 5.3 630A	Schneider Electric	COMPACT NSX	Curve_Micrologic_5.3	630	3	39,7	50

## TripUnitsCatalog
ID	L_zone_type	L_zone_curv_min	L_zone_curv_max	L_zone_Ki	L_zone_Ir	L_zone_tr	L_zone_t_accur	L_zone_I_accur	S_zone_type	S_zone_Isd	S_zone_I_accur	S_zone_tsd	I_zone_Ii	I_zone_I_accur	I_zone_ti
Unique name	Type of L zone (Table/Formula/None)	Min curve using the table	Max curve using the table	coefficient for calculation using the formula	Ir (if impossible to regulate =1)	Time tr L zone using formula(in format trmin, trmax), s	L zone time accuracy(in format -0.0, +0.0), %	L zone current accuracy	I2t of S zone (On/Off/None)	Range current S zone. Isd = Ir*... (in format Isdmin, Isdmax)	S zone time accuracy(in format -0.0, +0.0), %	Range time S zone (in format trmin, trmax), s	Range current I zone. Ii = In*... (in format Isdmin, Isdmax)	I zone time accuracy(in format -0.0, +0.0), %	Range time S zone (in format trmin, trmax), s
Curve_C_(DC)	Table	curves\mcb\Shneider\iC60H_DC\min.csv	curves\mcb\Shneider\iC60H_DC\max.csv	None	[ / 1.0 / ]	None	None	None	None	None	None	None	[ / 8.0 / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_B	Table	curves\mcb\Shneider\iC60\min.csv	curves\mcb\Shneider\iC60\max.csv	None	[ / 1.0 / ]	None	None	None	None	None	None	None	[ / 4.0 / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_C	Table	curves\mcb\Shneider\iC60\min.csv	curves\mcb\Shneider\iC60\max.csv	None	[ / 1.0 / ]	None	None	None	None	None	None	None	[ / 8.0 / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_D	Table	curves\mcb\Shneider\iC60\min.csv	curves\mcb\Shneider\iC60\max.csv	None	[ / 1.0 / ]	None	None	None	None	None	None	None	[ / 12.0 / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_TM16D_AC	Table	curves\mcb\Shneider\NSX\tm16d_min.csv	curves\mcb\Shneider\NSX\tm16d_max.csv	None	[ / 0.7, / 1.0 / ]	None	None	None	None	None	None	None	[ / 12.0 / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_TM63D_AC	Table	curves\mcb\Shneider\NSX\tm63d_min.csv	curves\mcb\Shneider\NSX\tm63d_max.csv	None	[ / 0.7, / 1.0 / ]	None	None	None	None	None	None	None	[ / 8.0 / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_MA_AC	None	None	None	None	None	None	None	None	None	None	None	None	[ / 6, / 14.0, / ]	[ / -20.0, / 20.0 / ]	[ / 0.002, / 0.01 / ]
Curve_Micrologic_2.2	Formula	None	None	1,5625	[ / 0.4, / 1.0 / ]	[ / 16.0 / ]	[ / -20.0, / 0.0 / ]	[ / 1.05, / 1.2 / ]	Off	[ / 1.5, / 10.0, / ]	[ / -10.0, / 10.0 / ]	[ / 0.02, / 0.08 / ]	[ / 15.0 / ]	[ / -15.0, / 15.0 / ]	[ / 0.01, / 0.05 / ]
Curve_Micrologic_5.3	Formula	None	None	1,5625	[ / 0.4, / 1.0 / ]	[ / 0.5, / 1.0, / 2.0, / 4.0, / 8.0, / 16.0 / ]	[ / -20.0, / 0.0 / ]	[ / 1.05, / 1.2 / ]	On	[ / 1.5, / 10.0, / ]	[ / -10.0, / 10.0 / ]	{ / "0": [ / 0.02, / 0.08 / ], / "0.1": [ / 0.08, / 0.14 / ], / "0.2": [ / 0.14, / 0.2 / ], / "0.3": [ / 0.23, / 0.32 / ], / "0.4": [ / 0.35, / 0.5 / ] / }	[ / 1.5, / 11.0, / ]	[ / -15.0, / 15.0 / ]	[ / 0.01, / 0.05 / ]

## Fuses
ID	Designation	Manufacturer	Series	In	Poles	P_loss_W	Icu	Curve_Min
Унікальна назва	Позначення	Виробник	Серія	Номинальный ток А	Количество полюсов	Мощность рассеяния, Вт	Відключаюча здатність кА	Кривая мин.
PNA000_6A_2P	PNA000 6A 2P	OEZ	Varius FH000	6	2	1,3	50	curves\fuse\OEZ\PNa000_Gg_6.csv
PNA000_10A_2P	PNA000 10A 2P	OEZ	Varius FH000	10	2	1	50	curves\fuse\OEZ\PNa000_Gg_10.csv
PNA000_16A_2P	PNA000 16A 2P	OEZ	Varius FH000	16	2	1,7	50	curves\fuse\OEZ\PNa000_Gg_16.csv
PNA000_20A_2P	PNA000 20A 2P	OEZ	Varius FH000	20	2	2,53	50	curves\fuse\OEZ\PNa000_Gg_20.csv
PNA000_25A_2P	PNA000 25A 2P	OEZ	Varius FH000	25	2	2,3	50	curves\fuse\OEZ\PNa000_Gg_25.csv
PNA000_32A_2P	PNA000 32A 2P	OEZ	Varius FH000	32	2	2,6	50	curves\fuse\OEZ\PNa000_Gg_32.csv
PNA000_40A_2P	PNA000 40A 2P	OEZ	Varius FH000	40	2	3,1	50	curves\fuse\OEZ\PNa000_Gg_40.csv
PNA000_50A_2P	PNA000 50A 2P	OEZ	Varius FH000	50	2	3,8	50	curves\fuse\OEZ\PNa000_Gg_50.csv
PNA000_63A_2P	PNA000 63A 2P	OEZ	Varius FH000	63	2	4,6	50	curves\fuse\OEZ\PNa000_Gg_63.csv
PNA000_80A_2P	PNA000 80A 2P	OEZ	Varius FH000	80	2	5,8	50	curves\fuse\OEZ\PNa000_Gg_80.csv
PNA000_100A_2P	PNA000 100A 2P	OEZ	Varius FH000	100	2	6,95	50	curves\fuse\OEZ\PNa000_Gg_100.csv
PNA000_125A_2P	PNA000 125A 2P	OEZ	Varius FH000	125	2	7,2	50	curves\fuse\OEZ\PNa000_Gg_125.csv
PNA000_160A_2P	PNA000 160A 2P	OEZ	Varius FH000	160	2	9	50	curves\fuse\OEZ\PNa000_Gg_160.csv

## Transformers
ID	Designation	Wind	Sn	Un_HV	Conn_HV	Un_LV	Conn_LV	Ukz	Pnh	Pkz	I0_pct
Унікальна назва	Позначення	Кол. Обмоток	Sном, кВА	Uном ВН, кВ	Група соед. ВН D/Y	Uном НН, кВ	Група соед. НН D/Y	Напряжение КЗ, %	Pхх, кВт	Pкз, кВт	Ток ХХ, %
TM_630/6_D/Yn-11	ТМ 630/6 D/Yn-11	2	630	6	D	0,4	Yn	5,5	1	8,8	2
TM_630/6_Y/Yn-0	ТМ 630/6 Y/Yn-0	2	630	6	Y	0,4	Yn	5,5	1	8,8	2